## Slide 1: TA-Modulator the only integrated valve works in market

## Slide 2: What is the ideal feature of control valve
Heating/Cooling coil
Control valve
Control is easy
The premise is The pressure drop of control valve should be constant
Notes: 该调节阀曲线为阀权度为1的时候的曲线

## Slide 3
Copyright © IMI Hydronic Engineering International SA. All rights reserved.
The feature of Coil/FCU/AHU
150 200
300
t=2.5 ºC
The diagram of q% and p%
10
0
130
120
110
100
90
80
70
60
50
40
30
20
50 100
250
q %
p%
200% q
110% p
Only 2.5 ºC
We can use control vale to to regulate flowrate

## Slide 4: Here we are
Modulator=Static valve+ dynamic pressure valve +control valve
Notes: For adjusting to a desired design flow rate, simply turn the setting wheel with your fingers to the setting value giving the flow according to flow/setting table or from HySelect or HyTools

## Slide 5: How it works
[DN 50]
Pressures ΔH = P1 – P3
Δp control plug = P1 – P2
Δp Dp-controller = P2 – P3
Measuring flow by measuring Δp P1 - P2(activated DpC)
Measuring ΔH by measuring Δp P1-P3 (deactivated DpC)
ΔH
p1
p2
p3
Pre-setting
P2
Spring pressed
Channel narrow
If P1
P1-P2 almost unchanged
P2-P3
The control is easy!!!

## Slide 6: How it works
[DN 50]
ΔH
p1
p2
p3
Pre-setting
1.Pre-setting KV of Control valve to design flowrate
2.Measure Δp control plug(P1-P2) to Calculate the flowrate to make sure it equals to design flowrate
TA is the only one who can measure P1 and P2 so as to calculate the flowrate to adjust

## Slide 7: main features
Long life reliability
AMETAL
Precise flow control
thanks to EQM characteristic on a pressure neutralized control plug
Fits to all projects and BMS systems
New fully configurable digital actuator TA-Slider 500 fits to all BMS systems
Automatic Balancing
Accurate pressure independent flow limitation for automatic hydronic balancing and high control stability.
True flow & pressure measurement
Full system optimisation with direct measurement of flow and available pressure.
Flexible connectivity male ISO 228 threads for multiple connections

## Slide 8: Some details
Venting screw
Pre-setting mechanism
Channel to transport p1 to the Δp controller
Shut off function for the pressure channel. Normally open
Control plug shaped for EQM characteristic
Inline Dp controller
Channel for pressure neutralized control plug
p1
p1
p1
p1

## Slide 9: Some details
Pre-setting mechanism
Channel to transport p2 to the PT port
Black PT port for measuring ΔH
Control plug shaped for EQM characteristic
Inline Dp controller
Channel to transport p1 to the Δp controller

## Slide 10: Thanks for your attention